## Feed Brackish Water-RO System
سامانه نمک زدایی آ ب لب شور مورد مطالعه- نمونه آب لب شور
Langelier's and Ryznar's Indices
Measured Water Characteristics
Calcium (mg/L as CaCO3) |  | 263.6
pH |  | 7.65
Temperature (ºC) |  | 19.7
Alkalinity (mg/L as CaCO3) |  | 47
TDS (mg/L) |  | 3229
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  | -0.59093
Ryznar's Stability Index |  | 8.8
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
Calculated Data
Ionic Strength |  | 0.080725
Activity Coefficient(m) |  | 0.78821
Activity Coefficient(d) |  | 0.38598
Ca(moles/L) |  | 0.002636
Alk(moles/L) |  | 0.00047
pK2 |  | 10.3813
K2 |  | 4.1567e-11
K2' |  | 1.0769e-10
pK2' |  | 9.9678
pKs |  | 8.2631
Ks |  | 5.4569e-09
Ks' |  | 3.6629e-08
pKs' |  | 7.4362
pCa |  | 2.5791
pHs |  | 8.2409
Site: Brackishwater Desalination System(BWRO)
Feed brackish water to RO desalination system

## 1 st stage RO
سامانه نمک زدایی آ ب لب شور مورد مطالعه-شورابه مرحله اول اسمز معکوس
Langelier's and Ryznar's Indices
Measured Water Characteristics
Calcium (mg/L as CaCO3) |  | 467
pH |  | 7.75
Temperature (ºC) |  | 20.19
Alkalinity (mg/L as CaCO3) |  | 83
TDS (mg/L) |  | 5407
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  | -0.065278
Ryznar's Stability Index |  | 7.9
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
Calculated Data
Ionic Strength |  | 0.13518
Activity Coefficient(m) |  | 0.75955
Activity Coefficient(d) |  | 0.33284
Ca(moles/L) |  | 0.00467
Alk(moles/L) |  | 0.00083
pK2 |  | 10.3763
K2 |  | 4.204e-11
K2' |  | 1.2631e-10
pK2' |  | 9.8986
pKs |  | 8.2688
Ks |  | 5.3846e-09
Ks' |  | 4.8606e-08
pKs' |  | 7.3133
pCa |  | 2.3307
pHs |  | 7.8153
Site: Brackishwater Desalination System(BWRO)
1st stage RO brine

## 2 nd stage RO
سامانه نمک زدایی آ ب لب شور مورد مطالعه-شورابه مرحله دوم اسمز معکوس
Langelier's and Ryznar's Indices
Measured Water Characteristics
Calcium (mg/L as CaCO3) |  | 1120
pH |  | 7.49
Temperature (ºC) |  | 17
Alkalinity (mg/L as CaCO3) |  | 126
TDS (mg/L) |  | 9579
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  | 0.079614
Ryznar's Stability Index |  | 7.3
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
Calculated Data
Ionic Strength |  | 0.23948
Activity Coefficient(m) |  | 0.73021
Activity Coefficient(d) |  | 0.2843
Ca(moles/L) |  | 0.0112
Alk(moles/L) |  | 0.00126
pK2 |  | 10.4093
K2 |  | 3.8964e-11
K2' |  | 1.3705e-10
pK2' |  | 9.8631
pKs |  | 8.2311
Ks |  | 5.8734e-09
Ks' |  | 7.2665e-08
pKs' |  | 7.1387
pCa |  | 1.9508
pHs |  | 7.4104
Site: Brackishwater Desalination System(BWRO)
2nd stage RO brine

## 1 st Stage RO-Feed TDS=4142
سامانه نمک زدایی آ ب لب شور مورد مطالعه- نمونه آب لب شور ورودی به سامانه
Langelier's and Ryznar's Indices
Measured Water Characteristics
Calcium (mg/L as CaCO3) |  | 434.4
pH |  | 7.5
Temperature (ºC) |  | 23
Alkalinity (mg/L as CaCO3) |  | 49.6
TDS (mg/L) |  | 4142
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  | -0.46048
Ryznar's Stability Index |  | 8.4
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
Calculated Data
Ionic Strength |  | 0.10355
Activity Coefficient(m) |  | 0.77705
Activity Coefficient(d) |  | 0.36458
Ca(moles/L) |  | 0.004344
Alk(moles/L) |  | 0.000496
pK2 |  | 10.3492
K2 |  | 4.475e-11
K2' |  | 1.2274e-10
pK2' |  | 9.911
pKs |  | 8.3021
Ks |  | 4.9878e-09
Ks' |  | 3.7525e-08
pKs' |  | 7.4257
pCa |  | 2.3621
pHs |  | 7.9605
Site: Brackishwater Desalination System(BWRO)
Feed brackish water to RO desalination system adding NaCl

## 1 Stage of RO-Feed TDS=6848
سامانه نمک زدایی آ ب لب شور مورد مطالعه- شورابه مرحله اول
Langelier's and Ryznar's Indices
Measured Water Characteristics
Calcium (mg/L as CaCO3) |  | 733.2
pH |  | 7.85
Temperature (ºC) |  | 23.1
Alkalinity (mg/L as CaCO3) |  | 77.6
TDS (mg/L) |  | 6848
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  | 0.23908
Ryznar's Stability Index |  | 7.4
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
Calculated Data
Ionic Strength |  | 0.1712
Activity Coefficient(m) |  | 0.75092
Activity Coefficient(d) |  | 0.31796
Ca(moles/L) |  | 0.007332
Alk(moles/L) |  | 0.000776
pK2 |  | 10.3483
K2 |  | 4.4846e-11
K2' |  | 1.4104e-10
pK2' |  | 9.8507
pKs |  | 8.3033
Ks |  | 4.9742e-09
Ks' |  | 4.9202e-08
pKs' |  | 7.308
pCa |  | 2.1348
pHs |  | 7.6109
Site: Brackishwater Desalination System(BWRO)
1st stage RO brine

## 1st stage RO-Desalinated Water
سامانه نمک زدایی آ ب لب شور مورد مطالعه-آب شیرین مرحله اول اسمز معکوس
Langelier's and Ryznar's Indices
Measured Water Characteristics
Calcium (mg/L as CaCO3) |  | 4.16
pH |  | 7.87
Temperature (ºC) |  | 20.46
Alkalinity (mg/L as CaCO3) |  | 10
TDS (mg/L) |  | 29
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  | -2.3794
Ryznar's Stability Index |  | 12.6
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
Calculated Data
Ionic Strength |  | 0.000725
Activity Coefficient(m) |  | 0.9692
Activity Coefficient(d) |  | 0.88237
Ca(moles/L) |  | 4.16e-05
Alk(moles/L) |  | 0.0001
pK2 |  | 10.3737
K2 |  | 4.2301e-11
K2' |  | 4.7939e-11
pK2' |  | 10.3193
pKs |  | 8.272
Ks |  | 5.3451e-09
Ks' |  | 6.8652e-09
pKs' |  | 8.1633
pCa |  | 4.3809
pHs |  | 10.2494
Site: Brackishwater Desalination System(BWRO)
1st stage RO desalinated water(Permeate)

## 2 nd stage RO-Desalinated Water
سامانه نمک زدایی آ ب لب شور مورد مطالعه- شیرین مرحله دوم اسمز معکوس
Langelier's and Ryznar's Indices
Measured Water Characteristics
Calcium (mg/L as CaCO3) |  | 23.68
pH |  | 7.55
Temperature (ºC) |  | 20.63
Alkalinity (mg/L as CaCO3) |  | 12
TDS (mg/L) |  | 279
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  | -1.9891
Ryznar's Stability Index |  | 11.5
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
Calculated Data
Ionic Strength |  | 0.006975
Activity Coefficient(m) |  | 0.9138
Activity Coefficient(d) |  | 0.69728
Ca(moles/L) |  | 0.0002368
Alk(moles/L) |  | 0.00012
pK2 |  | 10.372
K2 |  | 4.2465e-11
K2' |  | 6.09e-11
pK2' |  | 10.2154
pKs |  | 8.2741
Ks |  | 5.3204e-09
Ks' |  | 1.0943e-08
pKs' |  | 7.9609
pCa |  | 3.6256
pHs |  | 9.5391
Site: Brackishwater Desalination System(BWRO)
2nd stage RO desalinated water(Permeate)

## RO-Pilot1(Brine)
پایلوت- نمونه خوراک برداشتی از شورابه مرحله اول اسمز معکوس سامانه
Langelier's and Ryznar's Indices
Measured Water Characteristics
Calcium (mg/L as CaCO3) |  | 80.8
pH |  | 7.85
Temperature (ºC) |  | 25.03
Alkalinity (mg/L as CaCO3) |  | 142.6
TDS (mg/L) |  | 7221
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  | -0.415
Ryznar's Stability Index |  | 8.7
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
Calculated Data
Ionic Strength |  | 0.18053
Activity Coefficient(m) |  | 0.7506
Activity Coefficient(d) |  | 0.31742
Ca(moles/L) |  | 0.000808
Alk(moles/L) |  | 0.001426
pK2 |  | 10.3307
K2 |  | 4.6696e-11
K2' |  | 1.4711e-10
pK2' |  | 9.8324
pKs |  | 8.3261
Ks |  | 4.7195e-09
Ks' |  | 4.684e-08
pKs' |  | 7.3294
pCa |  | 3.0926
pHs |  | 8.265
Site : RO Pilot Desalination System
Brine TDS=7721

## RO-Pilot1(Permeate)
پایلوت- نمونه آب شیرین تولیدی از اسمز معکوس پایلوت
Langelier's and Ryznar's Indices
Measured Water Characteristics
Calcium (mg/L as CaCO3) |  | 3.84
pH |  | 7.5
Temperature (ºC) |  | 24.78
Alkalinity (mg/L as CaCO3) |  | 10.2
TDS (mg/L) |  | 762
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  | -2.9112
Ryznar's Stability Index |  | 13.3
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
Calculated Data
Ionic Strength |  | 0.01905
Activity Coefficient(m) |  | 0.87282
Activity Coefficient(d) |  | 0.58035
Ca(moles/L) |  | 3.84e-05
Alk(moles/L) |  | 0.000102
pK2 |  | 10.3329
K2 |  | 4.6457e-11
K2' |  | 8.005e-11
pK2' |  | 10.0966
pKs |  | 8.3231
Ks |  | 4.7517e-09
Ks' |  | 1.4108e-08
pKs' |  | 7.8505
pCa |  | 4.4157
pHs |  | 10.4112
Site : RO Pilot Desalination System
Permeate TDS=762

## R0-Pilot2(Feed)
پایلوت- نمونه خوراک با TDS=1712
Langelier's and Ryznar's Indices
Measured Water Characteristics
Calcium (mg/L as CaCO3) |  | 109.12
pH |  | 7.82
Temperature (ºC) |  | 16.56
Alkalinity (mg/L as CaCO3) |  | 209.2
TDS (mg/L) |  | 1712
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  | -0.13138
Ryznar's Stability Index |  | 8.1
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
Calculated Data
Ionic Strength |  | 0.0428
Activity Coefficient(m) |  | 0.82311
Activity Coefficient(d) |  | 0.45903
Ca(moles/L) |  | 0.0010912
Alk(moles/L) |  | 0.002092
pK2 |  | 10.4141
K2 |  | 3.8541e-11
K2' |  | 8.3961e-11
pK2' |  | 10.0759
pKs |  | 8.2259
Ks |  | 5.9442e-09
Ks' |  | 2.8211e-08
pKs' |  | 7.5496
pCa |  | 2.9621
pHs |  | 7.9514
Site : RO Pilot Desalination System
Feed Water TDS=1712

## RO-Pilot2(Permeate)
پایلوت- نمونه آب شیرین تولیدی از آب شبکه
Langelier's and Ryznar's Indices
Measured Water Characteristics
Calcium (mg/L as CaCO3) |  | 3.92
pH |  | 7.46
Temperature (ºC) |  | 16.95
Alkalinity (mg/L as CaCO3) |  | 118
TDS (mg/L) |  | 7.6
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  | -1.7892
Ryznar's Stability Index |  | 11
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
Calculated Data
Ionic Strength |  | 0.00019
Activity Coefficient(m) |  | 0.98355
Activity Coefficient(d) |  | 0.93581
Ca(moles/L) |  | 3.92e-05
Alk(moles/L) |  | 0.00118
pK2 |  | 10.4099
K2 |  | 3.8915e-11
K2' |  | 4.1585e-11
pK2' |  | 10.3811
pKs |  | 8.2305
Ks |  | 5.8814e-09
Ks' |  | 6.716e-09
pKs' |  | 8.1729
pCa |  | 4.4067
pHs |  | 9.2492
Site : RO Pilot Desalination System
Permeate TDS=7.6

## RO-Pilot3(Feed)
پایلوت- نمونه خوراک برداشتی از شورابه مرحله اول اسمز معکوس سامانه
Langelier's and Ryznar's Indices
Measured Water Characteristics
Calcium (MG/L as CaCO3) |  | 484
pH |  | 6.95
Temperature (Degrees Celcius) |  | 10.3
Alkalinity (MG/L as CaCO3) |  | 22
Total Dissolved Solids(MG/L) |  | 6999
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  | -1.7243
Ryznar's Stability Index |  | 10.4
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
Calculated Data
Ionic Strength |  | 0.17498
Activity Coefficient(m) |  | 0.73527
Activity Coefficient(d) |  | 0.29227
Ca(moles/L) |  | 0.00484
Alk(moles/L) |  | 0.00022
pK2 |  | 10.4866
K2 |  | 3.2611e-11
K2' |  | 1.1158e-10
pK2' |  | 9.9524
pKs |  | 8.1518
Ks |  | 7.0494e-09
Ks' |  | 8.2526e-08
pKs' |  | 7.0834
pCa |  | 2.3152
pHs |  | 8.6743
Site : RO Pilot Desalination System
Feed TDS=6999

## RO-Pilot3(Permeate)
پایلوت- نمونه آب شیرین تولیدی از شورابه مرحله دوم اسمز معکوس سامانه
Langelier's and Ryznar's Indices
Measured Water Characteristics
Calcium (mg/L as CaCO3) |  | 134
pH |  | 7.3
Temperature (ºC) |  | 10.5
Alkalinity (mg/L as CaCO3) |  | 54
TDS (mg/L) |  | 2740
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  | -1.3836
Ryznar's Stability Index |  | 10.1
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
Calculated Data
Ionic Strength |  | 0.0685
Activity Coefficient(m) |  | 0.78915
Activity Coefficient(d) |  | 0.38782
Ca(moles/L) |  | 0.00134
Alk(moles/L) |  | 0.00054
pK2 |  | 10.4842
K2 |  | 3.2797e-11
K2' |  | 8.4566e-11
pK2' |  | 10.0728
pKs |  | 8.1542
Ks |  | 7.0111e-09
Ks' |  | 4.6615e-08
pKs' |  | 7.3315
pCa |  | 2.8729
pHs |  | 8.6836
Site : RO Pilot Desalination System
Permeate TDS=2740

## RO-Pilot4(Brine)
پایلوت- شورابه مرحله دوم سامانه
Langelier's and Ryznar's Indices
Measured Water Characteristics
Calcium (mg/L as CaCO3) |  | 71.12
pH |  | 7.83
Temperature (ºC) |  | 22.76
Alkalinity (mg/L as CaCO3) |  | 130
TDS (mg/L) |  | 9723
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  | -0.61963
Ryznar's Stability Index |  | 9.1
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
Calculated Data
Ionic Strength |  | 0.24308
Activity Coefficient(m) |  | 0.73641
Activity Coefficient(d) |  | 0.29409
Ca(moles/L) |  | 0.0007112
Alk(moles/L) |  | 0.0013
pK2 |  | 10.3515
K2 |  | 4.4519e-11
K2' |  | 1.5138e-10
pK2' |  | 9.8199
pKs |  | 8.2993
Ks |  | 5.0205e-09
Ks' |  | 5.8047e-08
pKs' |  | 7.2362
pCa |  | 3.148
pHs |  | 8.4496
Site : RO Pilot Desalination System
Brine TDS=9723

## RO-Pilot4(Permeate)
پایلوت- نمونه آب با TDS=1557
Langelier's and Ryznar's Indices
Measured Water Characteristics
Calcium (mg/L as CaCO3) |  | 2.4
pH |  | 8.16
Temperature (ºC) |  | 23.1
Alkalinity (mg/L as CaCO3) |  | 10
TDS (mg/L) |  | 1557
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  | -2.5984
Ryznar's Stability Index |  | 13.4
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
Calculated Data
Ionic Strength |  | 0.038925
Activity Coefficient(m) |  | 0.83381
Activity Coefficient(d) |  | 0.48335
Ca(moles/L) |  | 2.4e-05
Alk(moles/L) |  | 0.0001
pK2 |  | 10.3483
K2 |  | 4.4846e-11
K2' |  | 9.278e-11
pK2' |  | 10.0325
pKs |  | 8.3033
Ks |  | 4.9742e-09
Ks' |  | 2.1291e-08
pKs' |  | 7.6718
pCa |  | 4.6198
pHs |  | 10.7584
Site : RO Pilot Desalination System
Permeate TDS=1557

## RO-Pilot5(Feed)
پایلوت- شورابه مرحله دوم سامانه اسمز معکوس
Langelier's and Ryznar's Indices
Measured Water Characteristics
Calcium (mg/L as CaCO3) |  | 1120
pH |  | 7.77
Temperature (ºC) |  | 13.41
Alkalinity (mg/L as CaCO3) |  | 116.4
TDS (mg/L) |  | 9610
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  | 0.22947
Ryznar's Stability Index |  | 7.3
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
Calculated Data
Ionic Strength |  | 0.24025
Activity Coefficient(m) |  | 0.72578
Activity Coefficient(d) |  | 0.27747
Ca(moles/L) |  | 0.0112
Alk(moles/L) |  | 0.001164
pK2 |  | 10.4494
K2 |  | 3.5532e-11
K2' |  | 1.2806e-10
pK2' |  | 9.8926
pKs |  | 8.1886
Ks |  | 6.4768e-09
Ks' |  | 8.4128e-08
pKs' |  | 7.0751
pCa |  | 1.9508
pHs |  | 7.5405
Site : RO Pilot Desalination System
Feed TDS=9610

## RO-Pilot5(Brine)
پایلوت- نمونه شورابه با TDS=12660
Langelier's and Ryznar's Indices
Measured Water Characteristics
Calcium (mg/L as CaCO3) |  | 1407.2
pH |  | 4.08
Temperature (ºC) |  | 15.99
Alkalinity (mg/L as CaCO3) |  | 0.008
TDS (mg/L) |  | 12660
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  | -7.4773
Ryznar's Stability Index |  | 19
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
Calculated Data
Ionic Strength |  | 0.3165
Activity Coefficient(m) |  | 0.72154
Activity Coefficient(d) |  | 0.27105
Ca(moles/L) |  | 0.014072
Alk(moles/L) |  | 8e-08
pK2 |  | 10.4203
K2 |  | 3.7993e-11
K2' |  | 1.4017e-10
pK2' |  | 9.8533
pKs |  | 8.2192
Ks |  | 6.0372e-09
Ks' |  | 8.2176e-08
pKs' |  | 7.0853
pCa |  | 1.8516
pHs |  | 11.5573
Site : RO Pilot Desalination System
Brine from Second Stage of RO adding NaCl TDS=12660

## RO-Pilot6(Feed)
پایلوت- نمونه شورابه با TDS=12739
Langelier's and Ryznar's Indices
Measured Water Characteristics
Calcium (mg/L as CaCO3) |  | 76
pH |  | 7.8
Temperature (ºC) |  | 24.88
Alkalinity (mg/L as CaCO3) |  | 110.2
TDS (mg/L) |  | 12739
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  | -0.66122
Ryznar's Stability Index |  | 9.1
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
Calculated Data
Ionic Strength |  | 0.31848
Activity Coefficient(m) |  | 0.73197
Activity Coefficient(d) |  | 0.28707
Ca(moles/L) |  | 0.00076
Alk(moles/L) |  | 0.001102
pK2 |  | 10.3321
K2 |  | 4.6553e-11
K2' |  | 1.6217e-10
pK2' |  | 9.79
pKs |  | 8.3243
Ks |  | 4.7388e-09
Ks' |  | 5.7505e-08
pKs' |  | 7.2403
pCa |  | 3.1192
pHs |  | 8.4612
Site : RO Pilot Desalination System
Feed TDS=12739 Adding NaCl to brine

## Electro.4+Chemical Percip.
پایلوت- فرآیند توام الکتروکواگولاسیون مرحله چهارم و ترسیب شیمیایی
Langelier's and Ryznar's Indices
Measured Water Characteristics
Calcium (mg/L as CaCO3) |  | 126.2
pH |  | 9
Temperature (ºC) |  | 10.15
Alkalinity (mg/L as CaCO3) |  | 72.2
TDS (mg/L) |  | 8055
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  | 0.23488
Ryznar's Stability Index |  | 8.5
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
Calculated Data
Ionic Strength |  | 0.20137
Activity Coefficient(m) |  | 0.72868
Activity Coefficient(d) |  | 0.28193
Ca(moles/L) |  | 0.001262
Alk(moles/L) |  | 0.000722
pK2 |  | 10.4885
K2 |  | 3.2471e-11
K2' |  | 1.1517e-10
pK2' |  | 9.9386
pKs |  | 8.1501
Ks |  | 7.0782e-09
Ks' |  | 8.9051e-08
pKs' |  | 7.0504
pCa |  | 2.8989
pHs |  | 8.7651
Site : Pilot -Electrocoagulation 4+Chemical Precipitation
TDS=8055

## Sedimentation Tank
پایلوت- مخزن ته نشینی با تنظیم pH و اضافه کردن EDTA
Langelier's and Ryznar's Indices
Measured Water Characteristics
Calcium (mg/L as CaCO3) |  | 449
pH |  | 6.4
Temperature (ºC) |  | 11.8
Alkalinity (mg/L as CaCO3) |  | 43.2
TDS (mg/L) |  | 7264
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  | -1.9777
Ryznar's Stability Index |  | 10.4
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
Calculated Data
Ionic Strength |  | 0.1816
Activity Coefficient(m) |  | 0.7353
Activity Coefficient(d) |  | 0.29232
Ca(moles/L) |  | 0.00449
Alk(moles/L) |  | 0.000432
pK2 |  | 10.4684
K2 |  | 3.4012e-11
K2' |  | 1.1635e-10
pK2' |  | 9.9342
pKs |  | 8.1696
Ks |  | 6.7672e-09
Ks' |  | 7.9192e-08
pKs' |  | 7.1013
pCa |  | 2.3478
pHs |  | 8.3777
Site :Pilot- Sedimentation Tank with EDTA injection
TDS=7264

## Ultrafiltration
پایلوت- فرآیند اولترافیلتراسیون
Langelier's and Ryznar's Indices
Measured Water Characteristics
Calcium (mg/L as CaCO3) |  | 301
pH |  | 6.4
Temperature (ºC) |  | 11.38
Alkalinity (mg/L as CaCO3) |  | 43.2
TDS (mg/L) |  | 6351
Calculated Langelier's Index and Ryznar's Stability Index
Langelier's Saturation Index |  | -2.1436
Ryznar's Stability Index |  | 10.7
If the LSI index is negative or the Ryznar >6.0 calcium carbonate is soluble and deposition unlikely.
If the LSI index is positive or the Ryznar < 6.0 calcium carbonate deposition is likely.
Calculated Data
Ionic Strength |  | 0.15877
Activity Coefficient(m) |  | 0.74135
Activity Coefficient(d) |  | 0.30205
Ca(moles/L) |  | 0.00301
Alk(moles/L) |  | 0.000432
pK2 |  | 10.4734
K2 |  | 3.3618e-11
K2' |  | 1.113e-10
pK2' |  | 9.9535
pKs |  | 8.1646
Ks |  | 6.845e-09
Ks' |  | 7.5026e-08
pKs' |  | 7.1248
pCa |  | 2.5214
pHs |  | 8.5436
Site : Pilot -Ultrafiltration
TDS=6351